Chapter 24   WATER, SEWERS AND SEWAGE DISPOSAL

*DIVISION 3. WATER - TECHNICAL REGULATIONS

Sec. 24-57. Location of water mains.

All water mains in any street of the city which run east and west shall be located on a

line 15 feet south of the center of such street, and all water mains in any street of the city

which runs north and south shall be located on a line 15 feet west of the center of such street.

(Code 1970, § 24-55; Ord. No. 81-11-2, § 24-57, 11-3-81)

Sec. 24-58. Diameter of pipes.

No pipe of less than three-fourths of an inch in diameter shall be permitted to be placed

underground in connection with the city water system.

(Code 1970, § 24-56; Ord. No. 81-11-2, § 24-58, 11-3-81)

Sec. 24-59. Depth of service pipes below ground.

All water service pipes shall be laid at least 48 inches below the surface of the ground.

(Code 1970, § 24-57; Ord. No. 81-11-2, § 24-59, 11-3-81)

Sec. 24-60. Water service in sewer trench.

No water service pipes shall be permitted to be laid in any sewer trench unless such

water service pipe shall be above the sewer and shall be shelved not less than 18 inches

above and to one side of the sewer. If such vertical clearance cannot be obtained, the water

service pipe shall be permitted to be laid in the sewer trench provided that the sewer is

constructed of pressure rated material such as cast iron or PVC.

(Code 1970, § 24-58; Ord. No. 81-11-2, § 24-60, 11-3-81)

Sec. 24-61. Iron water pipes, couplings, soldering.

Where iron water pipes are in use in houses, a brass coupling must be used for

connecting the lead with the iron pipe. In no case shall lead be soldered in iron.

(Code 1970, § 24-59; Ord. No. 81-11-2, § 24-61, 11-3-81)

Sec. 24-62. Curb cocks.

A curb cock sufficiently strong to resist the pressure and ram of the water shall be

placed in every attachment to the water system. In streets such cock shall be within one foot of

the property line. Each house shall have a separate meter and a separate stopcock, the latter

to be placed four feet below the surface of the ground. Such cock shall have a strong and

suitable T-lead, all enclosed in iron casing extending even with the surface of the ground and

covered with a tightfitting iron lid with the letter "W" on it. The pattern of all appurtenances shall

be subject to the approval of the superintendent.

(Code 1970, § 24-60; Ord. No. 81-11-2, § 24-62, 11-3-81)

Sec. 24-63. Pipes to be connected by licensed plumber.

No person other than a plumber licensed by the state shall connect water service pipes

with the city water system.

(Code 1970, § 24-61; Ord. No. 81-11-2, § 24-63, 11-3-81)

Sec. 24-64. Tap, connections to be supervised by superintendent.

All tapping of pipes connected with the city water system and all connections with the

water mains shall be done under the supervision and control of the superintendent of water

and sewers.

(Code 1970, § 24-62; Ord. No. 81-11-2, § 24-64, 11-3-81)

Sec. 24-65. Where taps to be made.

Water main pipes must be tapped in the body, and no nearer than 15 inches from

either end of the pipe, and/or the opening of the hub or bell. No taps shall be made nearer

than two feet from each other.

(Code 1970, § 24-63; Ord. No. 81-11-2, § 24-65, 11-3-81)

Sec. 24-66. Taps to be approved before burial.

Tapping work performed on city water mains or sewers shall not be covered up until

such work has been inspected and approved by the superintendent of water and sewers.

(Code 1970, § 24-64; Ord. No. 81-11-2, § 24-66, 11-3-81)

DIVISION 4. CROSS CONNECTION CONTROL

Sec. 24-66.1. Definitions.

The following words, terms and phrases, when used in this division, shall have the

meanings ascribed to them in this section, except where the context clearly indicates a

different meaning:

Agency means the state environmental protection agency.

Approved means backflow prevention devices or methods approved by the Research

Foundation for Cross Connection Control of the University of Southern California, American

Water Works Association (AWWA), American National Standards Institute, Association of

State Sanitary Engineers (ASSE) or certified by the National Sanitation Foundation (NSF).

Auxiliary water system means any water source or system on or available to the

premises other than the public water supply system and includes the water supplied by the

system. These auxiliary waters may include water from another purveyor's public water supply

system; or water from a source such as wells, lakes or streams, or process fluids; or used

water. These waters may be polluted or contaminated or objectionable or constitute a water

source or system over which the water purveyor does not have control.

Backflow means the flow of water or other liquids, mixtures, or substances into the

distribution pipes of a potable water system from any source other than the intended source of

the potable water supply.

Backflow prevention device means any device, method or type of construction intended

to prevent backflow into a potable water system. All devices used for backflow prevention in

the state must meet the standards of the state plumbing code and the state environmental

protection agency.

Consumer or customer means the owner, official custodian or person in control of any

premises supplied by or in any manner connected to a public water system.

Consumer's water system means any water system located on the customer's

premises. A building plumbing system is considered to be a customer's water system.

Contamination means an impairment of the quality of the water by entrance of any

substance to a degree which could create a health hazard.

Cross connection means any physical connection or arrangement between two

otherwise separate piping systems, one of which contains potable water and the other a

substance of unknown or questionable safety or quality, whereby there may be a flow from

one system into another.

Direct cross connection means a cross connection formed when a water system is

physically joined to a source of unknown or unsafe substance.

Double check valve assembly means an assembly composed of single, independently

acting check valves approved under ASSE Standard 1015. A double check valve assembly

must include tight shutoff valves located at each end of the assembly and suitable connections

for testing the watertightness of each check valve.

Fixed proper air gap means the unobstructed vertical distance through the free

atmosphere between the water discharge point and the flood level rim of the receptacle.

Health hazard means any condition, device or practice in a water system or its

operation resulting in a real or potential danger to the health and well-being of consumers. The

word "severe" as used to qualify health hazard means a hazard to the health of the user that

could be expected to result in death or significant reduction in the quality of life.

Indirect cross connection means a cross connection through which an unknown

substance can be forced, drawn by vacuum or otherwise introduced into a safe potable water

system.

Inspection means a plumbing inspection to examine carefully and critically all materials,

fixtures, piping and appurtenances, appliances and installations of a plumbing system for

compliance with requirements of the Illinois Plumbing Code, 77 Ill. Adm. Code 890.

Nonpotable water means water not safe for drinking, personal or culinary use as

determined by the requirements of 35 Ill. Adm. Code 604.

Plumbing means the actual installation, repair, maintenance, alteration or extension of

a plumbing system by any person. Plumbing includes all piping, fixtures, appurtenances and

appliances for a supply of water for all purposes, including without limitation lawn sprinkler

systems, from the source of a private water supply on the premises or from the main in the

street, alley or at the curb to, within and about any building or buildings where a person or

persons live, work or assemble. Plumbing includes all piping, from discharge of pumping units

to and including pressure tanks in water supply systems. Plumbing includes all piping, fixtures,

appurtenances and appliances for a building drain and a sanitary drainage and related

ventilation system of any building or buildings where a person lives, works or assembles from

the point of connection of such building drain to the building sewer or private sewage disposal

system five feet beyond the foundation walls.

Pollution means the presence of any foreign substance--organic, inorganic,

radiological, or biological--in water that tends to degrade its quality so as to constitute a hazard

or impair the usefulness of the water.

Potable water means water which meets the requirements of 35 Ill. Adm. Code 604 for

drinking, culinary and domestic purposes.

Potential cross connection means a fixture or appurtenance with threaded hose

connection, tapered spout or other connection which would facilitate extension of the water

supply line beyond its legal termination point.

Process fluids means any fluid or solution which may be chemically, biologically or

otherwise contaminated or polluted in a form or concentration such as would constitute a

health, pollutional or system hazard if introduced into the public or a consumer's potable water

system. This includes but is not limited to:

(1) Polluted or contaminated waters.

(2) Process waters.

(3) Used waters originating from the public water supply system which may have

deteriorated in sanitary quality.

(4) Cooling waters.

(5) Questionable or contaminated natural waters taken from wells, lakes, streams,

or irrigation systems.

(6) Chemicals in solution or suspension.

(7) Oils, gases, acids, alkalis and other liquid and gaseous fluids used in industrial

or other processes, or for firefighting purposes.

Public water supply means all mains, pipes and structures through which water is

obtained and distributed to the public, including wells and well structures, intakes and cribs,

pumping stations, treatment plants, reservoirs, storage tanks and appurtenances, collectively

or severally, actually used or intended for use for the purpose of furnishing water for drinking

or general domestic use and which serve at least 15 service connections or which regularly

serve at least 25 persons at least 60 days per year. A public water supply is either a

community water supply or a noncommunity water supply.

Reduced pressure principle backflow prevention device means a device containing a

minimum of two independently acting check valves together with an automatically operated

pressure differential relief valve located between the two check valves and approved under

ASSE Standard 1013. During normal flow and at the cessation of normal flow, the pressure

between these two checks shall be less than the supply pressure. In case of leakage of either

check valve, the differential relief valve, by discharging to the atmosphere, shall operate to

maintain the pressure between the check valves at less than the supply pressure. The unit

must include tightly closing shutoff valves located at each end of the device, and each device

shall be fitted with properly located test cocks.

Service connection means the opening, including all fittings and appurtenances, at the

water main through which water is supplied to the user.

Survey means the collection of information pertaining to a customer's piping system

regarding the location of all connections to the public water supply system and must include

the location, type and most recent inspection and testing date of all cross connection control

devices and methods located within that customer's piping system. The survey must be in

written form, and should not be an actual plumbing inspection.

System hazard means a condition through which an aesthetically objectionable or

degrading material not dangerous to health may enter the public water supply system or a

consumer's potable water system.

Used water means any water supplied by a public water supply system to a consumer's

water system after it has passed through the service connection and is no longer under the

control of the water supply official custodian.

Water purveyor means the owner or official custodian of a public water system.

(Ord. No. 86-7-1, § 2, 7-1-86; Ord. No. 86-7-1A, 2-17-87)

Cross references: Definitions and rules of construction generally, § 1-2.

Sec. 24-66.2. General policy.

(a) Purpose. The purposes of the provisions of this division are:

(1) To protect the public water supply system from contamination or pollution by

isolating within the customer's water system contaminants or pollutants which

could backflow through the service connection into the public water supply

system.

(2) To promote the elimination or control of existing cross connections, actual or

potential, between the public or consumer's potable water system and

nonpotable water systems, plumbing fixtures and sources or systems containing

substances of unknown or questionable safety.

(3) To provide for the maintenance of a continuing program of cross connection

control which will prevent the contamination or pollution of the public and

consumer's potable water systems.

(b) Application. This division shall apply to all premises served by the public potable water

supply system of the city.

(c) Policy. The owner or official custodian shall be responsible for protection of the public

water supply system from contamination due to backflow or backsiphonage of

contaminants through the customer's water service connection. If, in the judgment of

the superintendent of water or his authorized representative, an approved backflow

prevention device is necessary for the safety of the public water supply system, the

superintendent of water shall give notice to the consumer to install such approved

backflow prevention device at each service connection to the premises. The consumer

shall immediately install such approved device or devices at his own expense; failure,

refusal or inability on the part of the consumer to install such device or devices

immediately shall constitute grounds for discontinuing water service to the premises

until such device or devices have been installed. The consumer shall retain records of

installation, maintenance, testing and repair as required in section 24-66.5(e)(4) for a

period of at least five years.

(Ord. No. 86-7-1, § 1, 7-1-86)

Sec. 24-66.3. Water system.

(a) The water system shall be considered as made up of two parts: the public water supply

system and the consumer's water system.

(b) The public water supply system shall consist of the source facilities and the distribution

system, and shall include all those facilities of the potable water system under the

control of the superintendent of water up to the point where the consumer's water

system begins.

(c) The source shall include all components of the facilities utilized in the production,

treatment, storage and delivery of water to the public water supply distribution system.

(d) The public water supply distribution system shall include the network of conduits used

to deliver water from the source to the consumer's water system.

(e) The consumer's water system shall include all parts of the facilities beyond the service

connection used to convey water from the public water supply distribution system to

points of use.

(Ord. No. 86-7-1, § 3, 7-1-86)

Sec. 24-66.4. Cross connection prohibited.

(a) Connections between potable water systems and other systems or equipment

containing water or other substances of unknown or questionable quality are prohibited

except when and where approved cross connection control devices or methods are

installed, tested and maintained to insure proper operation on a continuing basis.

(b) No physical connection shall be permitted between the potable portion of a supply and

any other water supply not of equal or better bacteriological and chemical quality as

determined by inspection and analysis by the agency.

(c) There shall be no arrangement or connection by which an unsafe substance may enter

a supply.

(Ord. No. 86-7-1, § 4, 7-1-86)

Sec. 24-66.5. Survey and investigations.

(a) It shall be the duty of the superintendent of water to cause surveys and investigations

to be made of industrial and other properties served by the public water supply to

determine whether actual or potential hazards to the public water supply may exist.

Such surveys and investigations shall be made a matter of public record and shall be

repeated at least every two years, or as often as the superintendent of water shall

deem necessary. Records of such surveys shall be maintained and available for review

for a period of at least five years.

(b) The consumer's premises shall be open at all reasonable times to the approved cross

connection control device inspector for the inspection of the presence or absence of

cross connections within the consumer's premises, and testing, repair and maintenance

of cross connection control devices within the consumer's premises.

(c) On request by the superintendent of water, or his authorized representative, the

consumer shall furnish information regarding the piping system or systems or water use

within the customer's premises. The consumer's premises shall be open at all

reasonable times to the superintendent of water for the verification of information

submitted by the inspection consumer to the public water supply custodian regarding

cross connection inspection results.

(d) It shall be the responsibility of the water consumer to arrange periodic surveys of water

use practices on his premises to determine whether there are actual or potential cross

connections to his water system through which contaminants or pollutants could

backflow into his or the public potable water system. All cross connection control or

other plumbing inspections must be conducted in accordance with section 3(1) of the

Illinois Plumbing License Law (Ill. Rev. Stat. ch. 111, § 1103(1)).

(e) It is the responsibility of the water consumer to prevent backflow into the public water

system by ensuring that:

(1) All cross connections are removed; or approved cross connection control

devices are installed for control of backflow and backsiphonage.

(2) Cross connection control devices shall be installed in accordance with the

manufacturer's instructions.

(3) Cross connection control devices shall be inspected at least annually by a

person approved by the agency as a cross connection control device inspector

(CCCDI). The inspection of mechanical devices shall include physical testing in

accordance with the manufacturer's instructions.

(4) Testing and records.

a. Each device shall be tested at least annually or more frequently if

recommended by the manufacturer.

b. Records submitted to the community public water supply shall be

available for inspection by agency personnel in accordance with section

4(d) of the Environmental Protection Act (Ill. Rev. Stat. ch. 111 1/2, §

1004(d)).

c. Each device shall have a tag attached listing the date of most recent

test, name of CCCDI, and type and date of repairs.

d. A maintenance log shall be maintained and include:

1. Date of each test;

2. Name and approval number of person performing the test;

3. Test results;

4. Repairs or servicing required;

5. Repairs and date completed; and

6. Servicing performed and date completed.

(Ord. No. 86-7-1, § 5, 7-1-86)

Sec. 24-66.6. Where protection is required.

(a) An approved backflow prevention device shall be installed on each service line to a

consumer's water system serving premises, where in the judgment of the

superintendent of water, actual or potential hazards to the public water supply system

exist.

(b) An approved backflow prevention device shall be installed on each service line to a

consumer's water system serving premises where the following conditions exist:

(1) Premises having an auxiliary water supply, unless such auxiliary supply is

accepted as an additional source by the superintendent of water and the source

is approved by the state environmental protection agency.

(2) Premises on which any substance is handled which can create an actual or

potential hazard to the public water supply system. This shall include premises

having sources or systems containing process fluids or waters originating from

the public water supply system which are no longer under the sanitary control of

the superintendent of water.

(3) Premises having internal cross connections that, in the judgment of the

superintendent of water, are not correctable or intricate plumbing arrangements

which make it impractical to determine whether or not cross connections exist.

(4) Premises where, because of security requirements or other prohibitions or

restrictions, it is impossible or impractical to make a complete cross connection

survey.

(5) Premises having a repeated history of cross connections being established or

reestablished.

(c) An approved backflow device shall be installed on all connections to the public water

supply as described in the Illinois Plumbing Code, 77 Ill. Adm. Code 890, and Illinois

Environmental Protection Agency Technical Policy Statements, 35 Ill. Adm. Code 680.

In addition, an approved backflow prevention device shall be installed on each service

line to a consumer's water system serving, but not necessarily limited to, the following

types of facilities unless the superintendent of water determines that no actual or

potential hazard to the public water supply system exist:

(1) Hospitals, mortuaries, clinics, nursing homes.

(2) Laboratories.

(3) Piers, docks, waterfront facilities.

(4) Sewage treatment plants, sewage pumping stations or storm- water pumping

stations.

(5) Food or beverage processing plants.

(6) Chemical plants.

(7) Metal plating industries.

(8) Petroleum processing or storage plants.

(9) Radioactive material processing plants or nuclear reactors.

(10) Car washes.

(11) Pumps for nonpotable water, chemicals or other substances.

(12) Potable water connections to boilers.

(13) Refrigerating unit condensers and cooling jackets.

(14) Bidets.

(Ord. No. 86-7-1, § 6, 7-1-86; Ord. No. 86-7-1A, 2-17-87)

Sec. 24-66.7. Type of protection required.

(a) The type of protection required under section 24-66.6 shall depend on the degree of

hazard which exists as follows:

(1) An approved fixed proper air gap separation shall be installed where the public

water supply system may be contaminated with substances that could cause a

severe health hazard.

(2) The minimum required air gap shall be measured vertically from the lowest end

of a potable water outlet to the flood rim or line of the fixture or receptacle into

which it discharges.

(3) The minimum required air gap shall be twice the effective opening of a potable

water outlet unless the outlet is a distance less than three times the effective

opening away from a wall or similar vertical surface, in which case the minimum

required air gap shall be three times the effective opening of the outlet. In no

case shall the minimum required air gap be less than one inch.

(4) An approved fixed proper air gap separation or an approved reduced pressure

principal backflow prevention device shall be installed where the public water

supply system may be contaminated with a substance that could cause a

system or health hazard.

(5) An approved fixed proper air gap separation or an approved reduced pressure

principal backflow prevention device shall be installed where the public water

supply system may be polluted with substances that could cause a pollution

hazard not dangerous to health.

(b) The type of protection required under section 24-66.6 of these regulations shall be an

approved fixed proper air gap separation or an approved reduced pressure principal

backflow prevention device.

(c) Where a public water supply or an auxiliary water supply is used for a fire protection

system, reduced pressure principal backflow preventers shall be installed on fire

sprinkler systems connected to the public water supply when:

(1) The sprinkler system contains antifreeze;

(2) Water is pumped into the system from another source; or

(3) There is a connection whereby another source can be connected to the

sprinkler system.

(Ord. No. 86-7-1, § 7, 7-1-86)

Sec. 24-66.8. Backflow prevention devices.

(a) All backflow prevention devices or methods required by these rules and regulations

shall be approved by the Research Foundation for Cross Connection Control of the

University of Southern California, American Water Works Association, American

Society of Sanitary Engineering, or American National Standards Institute or certified by

the National Sanitation Foundation to be in compliance with applicable industry

specification and shall be on the list of devices approved for use by the IL EPA.

(b) Installation of approved devices shall be made in accordance with 35 Ill. Adm. Code

653.802, and only as specified by the Research Foundation for Cross Connection

Control of the University of Southern California or applicable industry specifications.

Maintenance as recommended by the manufacturer of the device shall be performed.

Manufacturer's maintenance manual shall be available on-site.

(Ord. No. 86-7-1, § 8, 7-1-86)

Sec. 24-66.9. Inspection and maintenance.

(a) It shall be the duty of the consumer at any premises on which backflow prevention

devices required by this division are installed to have inspection, tests, maintenance

and repair made in accordance with the following schedule or more often where

inspections indicate a need or are specified in manufacturer's instructions.

(1) Fixed proper air gap separations shall be inspected at the time of installation

and at least annually thereafter.

(2) Double check valve assemblies shall be inspected and tested for tightness at

time of installation and at least annually thereafter, and required service

performed within 15 days.

(3) Reduced pressure principle backflow prevention devices shall be tested at the

time of installation and at least annually, or more frequently if recommended by

the manufacturer. Any service required on these devices shall be performed

within five days.

(b) Testing shall be performed by a person who has been approved by the agency as

competent to service the device. Proof of approval shall be in writing.

(c) Each device shall have a tag attached listing the date of most recent test or visual

inspection, name of tester, and type and date of repairs.

(d) A maintenance log shall be maintained and include:

(1) Date of each test or visual inspection;

(2) Name and approval number of person performing the test or visual inspection;

(3) Test results;

(4) Repairs or servicing required;

(5) Repairs and date completed; and

(6) Servicing performed and date completed.

(e) Whenever backflow prevention devices required by this division are found to be

defective, they shall be repaired or replaced at the expense of the consumer without

delay.

(f) B ackflow prevention devices shall not be bypassed, made inoperative, removed or

otherwise made ineffective without specific authorization by the superintendent of

water.

(Ord. No. 86-7-1, § 9, 7-1-86; Ord. No. 86-7-1A, 2-17-87)

Sec. 24-66.10. Booster pumps.

(a) Where a booster pump has been installed on the service line to or within any premises,

such pump shall be equipped with a low pressure cutoff device designed to shut off the

booster pump when the pressure in the service line on the suction side of the pump

drops to 20 psi or less.

(b) It shall be the duty of the water consumer to maintain the low pressure cutoff device in

proper working order and to certify to the superintendent of water, at least once a year,

that the device is operable.

(Ord. No. 86-7-1, § 10, 7-1-86)

Sec. 24-66.11. Violations, penalties, liabilities.

(a) The superintendent of water shall deny or discontinue, after reasonable notice to the

occupants thereof, the water service to any premises wherein any backflow prevention

device required by this division is not installed, tested, maintained and repaired in a

manner acceptable to the superintendent of water, or if it is found that the backflow

prevention device has been removed or bypassed, or if an unprotected cross

connection exists on the premises, or if a low pressure cutoff required by this division is

not installed and maintained in working order.

(b) Immediate disconnection with verbal notice can be effected by the superintendent of

water when the superintendent is assured that imminent danger of harmful

contamination of the public water system exists. Such action shall be followed by

written notification of the cause of disconnection.

(c) Water service to such premises shall not be restored until the consumer has corrected

or eliminated such conditions or defects in conformance with these regulations and to

the satisfaction of the superintendent of water, and the required reconnection fee as

outlined in article IV is paid.

(d) The consumer responsible for backsiphoned material or contamination through

backflow, if contamination of the potable water supply system occurs through an illegal

cross connection or an improperly installed, maintained or repaired device, or a device

which has been bypassed, must bear the cost of clean-up of the potable water supply

system.

(e) Any person found to be violating any provision of this division shall be served with

written notice stating the notice of the violation and providing a reasonable time limit for

the satisfactory correction thereof. The offender shall, within the period of time stated in

such notice, permanently cease all violation.

(f) A ny person who shall continue such violation after receipt of handwritten notice, as

provided above, shall upon conviction thereof, be punished by a fine of not to exceed

$500.00 for each violation. Each day in which any such violation shall continue shall be

deemed a separate offense.

(g) Any person violating any of the provisions of this division, in addition to the fine

provided, shall become liable to the city for any expense, loss or damage occasioned

by the city by reason of such violation, whether the same was caused before or after

notice.

(Ord. No. 86-7-1, § 11, 7-1-86)

Secs. 24-66.12--24-66.20. Reserved.

Chapter 24   WATER, SEWERS AND SEWAGE DISPOSAL

ARTICLE V. SEWERS

DIVISION 1. GENERALLY

Sec. 24-67. Damaging sewer--By taps or connections.

It shall be unlawful for any person, by himself or by his employees, to break, injure or

damage the public sewer by tapping or making connections to such sewer, or by any other act.

Any person violating this section shall be liable for all damages occasioned by such acts.

(Code 1970, § 24-65; Ord. No. 81-11-2, § 24-67, 11-3-81)

Sec. 24-68. Same--Injuring, removing certain equipment.

It shall be unlawful to break, injure, deface or remove any cap, or gate, iron plate or

flushing apparatus belonging to any manhole, or any apparatus belonging to any manhole,

vent or inlet of any sewer or drain.

(Code 1970, § 24-66; Ord. No. 81-11-2, § 24-68, 11-3-81)

Sec. 24-69. Obstructing, injuring sewer mouth.

It shall be unlawful to obstruct or injure the mouth of any sewer.

(Code 1970, § 24-67; Ord. No. 81-11-2, § 24-69, 11-3-81)

Sec. 24-70. Obstructing, changing sewer drain.

It shall be unlawful to obstruct or change any branch sewer or natural sewer drain

without first obtaining the consent of the city council.

(Code 1970, § 24-68; Ord. No. 81-11-2, § 24-70, 11-3-81)

Sec. 24-71. Depositing garbage, etc., in sewer, manhole, drain inlet.

It shall be unlawful to throw or deposit any garbage, butcher's offal, dead animal matter

or other obstruction into any sewer, manhole or sewer drain inlet in the city.

(Code 1970, § 24-69; Ord. No. 81-11-2, § 24-71, 11-3-81)

Cross references: Garbage and trash, ch. 11.

Sec. 24-72. Depositing corrosive, harmful, explosive substances.

It shall be unlawful to throw or deposit in the public sewers any corrosive or harmful

wastes or any wastes at a temperature higher than 140 degrees Fahrenheit or any explosives,

gasoline, oil, calcium carbide or other inflammable matter.

(Code 1970, § 24-70; Ord. No. 81-11-2, § 24-72, 11-3-81)

Cross references: Fire prevention and protection, ch. 9.

Sec. 24-73. Treatment of sewage, industrial wastes, polluted waters required

before discharge.

It shall be unlawful to discharge into any natural outlet within the city, or in any area

under the jurisdiction of the city, any sanitary sewage, industrial wastes or other polluted

waters, except where suitable treatment has been provided in accordance with the provisions

of this article.

(Code 1970, § 24-71; Ord. No. 81-11-2, § 24-73, 11-3-81)

Sec. 24-74. Applicant to bear construction expense; indemnification of city.

The applicant for sewer service shall pay all costs and expenses incidental to the

installation and connection of the building sewer, and the maintenance thereof, from the point

of connection to the public sewer of the city, or to the collector sewer of the city if located

within a right-of-way of the city, to the premises of the applicant. The owner or the person

installing the building sewer for such owner shall indemnify the city from any loss or damage

that may directly or indirectly be occasioned by such installation.

(Code 1970, § 24-72; Ord. No. 81-11-2, § 24-74, 11-3-81)

DIVISION 2. TECHNICAL REGULATIONS

Sec. 24-80. Definitions.

The following words, terms and phrases, when used in this division, shall have the

meanings ascribed to them in this section, except where the context clearly indicates a

different meaning:

Biochemical oxygen demand (BOD) means the quantity of oxygen, expressed in

milligrams per liter (mg/l), utilized in the biochemical oxidation of organic matter under standard

laboratory procedures in five days at 20 degrees Celsius.

Building drain means that part of the lowest horizontal piping of a drainage system

which receives the discharge from soil, waste and other drainage pipes inside the walls of a

building and conveys it to the building sewer beginning three feet outside the building wall.

Building drain, sanitary means a building drain which conveys sanitary or industrial

sewage only.

Building drain, storm means a building drain which conveys stormwater or other clear

water drainage, but no sanitary or industrial sewage.

Building sewer means the extension from the building drain to the public sewer or other

place of disposal.

Building sewer, sanitary means a building sewer which conveys sanitary or industrial

sewage only.

Building sewer, storm means a building sewer which conveys stormwater or other clear

water drainage but no sanitary or industrial sewage.

Classes of users means the division of wastewater treatment customers by waste

characteristics, and process or discharge similarities.

(1) Residential includes all dwelling units such as detached, semidetached and row

houses, mobile homes, garden and standard apartments and permanent

multifamily dwellings.

(2) Commercial includes transient lodging, retail and wholesale establishments or

places engaged in selling merchandise for personal, household or industrial

consumption and/or rendering services to others.

(3) Institutional includes social, charitable, religious and educational activities such

as schools, churches, hospitals, nursing homes, penal institutions and similar

institutional users.

(4) Governmental includes legislative, judicial, administrative and regulatory

activities of federal, state and local governments, such as courthouses, police

and fire stations, city halls and similar governmental users.

(5) Industrial includes manufacturing activities involving the mechanical or chemical

transformation of materials or substances into other products. These activities

occur in establishments usually described as plants, factories or mills and

characteristically use power machines and material handling equipment.

Combined sewage means a combination of both sanitary and industrial wastewater and

stormwater or surface water.

Combined sewer means a sewer intended to receive both wastewater and stormwater

or surface water.

Compatible pollutant means a pollutant which the treatment works is designed to treat

and includes biochemical oxygen demand, suspended solids, pH and fecal coliform bacteria,

or a pollutant which the plant is able to remove to a substantial degree, being 80 percent or

greater.

Fecal coliform means any of a number of organisms common to the intestinal tract of

man and animals, whose presence in sanitary sewage is an indicator of pollution.

Floatable oil means oil, fat or grease in a physical state such that it will separate by

gravity from wastewater by treatment in a pretreatment facility approved by the city.

Garbage means solid wastes from the domestic and commercial preparation, cooking

and dispensing of food, and from the commercial handling, storage and sale of produce.

Incompatible pollutant means any pollutant that is not defined as a compatible

pollutant, including nonbiodegradable dissolved solids.

Industrial cost recovery means recovery from the industrial users of a treatment works

of the grant amount allocable to treatment of wastes from such users, exclusive of interest.

Industrial cost recovery period means that period during which the grant amount

allocable to the treatment of wastes from industrial users is recovered from the industrial users

of such works. The industrial cost recovery period shall be equal to 30 years or the useful life

of the treatment works, whichever is less, as determined by the city.

Industrial user means any nongovernmental user of publicly owned treatment works,

identified in the Standard Industrial Classification Manual, 1972, Office of Management and

Budget, as amended and supplemented, under the following divisions:

(1) Division A: Agriculture, forestry and fishing.

(2) Division B: Mining.

(3) Division D: Manufacturing.

(4) Division E: Transportation, communications, electric, gas and sanitary services.

(5) Division I: Services.

A user in the divisions listed may be excluded if it is determined by the city that it will introduce

primarily segregated domestic wastes or wastes from sanitary conveniences.

Industrial wastes means any solid, liquid or gaseous substance discharged, permitted

to flow or escaping from any industrial, manufacturing, commercial or business establishment

or process or from the development, recovery or processing of any natural resource as distinct

from sanitary sewage.

Infiltration means the water entering a sewer system, including building drains and

sewers, from the ground, through such means as, but not limited to, defective pipes, pipe

joints, connections or manhole walls.

Infiltration/inflow means the total quantity of water from both infiltration and inflow

without distinguishing the sources.

Inflow means the water discharged into a sewer system, including building drains and

sewers, from such sources as, but not limited to, roof leaders, cellar, yard and area drains,

foundation drains, unpolluted cooling water discharges, drains from springs and swampy

areas, manhole covers, cross connections with storm sewers, and combined sewers, catch

basins, stormwaters, surface runoff, street wash waters or drainage.

Major contributing industry means an industry that either has:

(1) A flow of 50,000 gallons or more per average work day;

(2) A flow greater than five percent of the flow carried by the public sewer system

receiving the waste;

(3) In its waste a toxic pollutant in toxic amounts as defined in standards issued

under section 307(a) of PL 92-500; or

(4) A significant impact, either singly or in combination with other contributing

industries, on a treatment works or on the quality of effluent from that treatment

works.

Metered usage means the metered water usage of any individual customer, unless

separate metering of sewage flow is provided for the customer, wherein it shall mean metered

sewage flow of any individual customer.

Natural outlet means any outlet, including storm sewers and combined sewer

overflows, into a watercourse, pond, ditch, lake or other body of surface water or groundwater.

Nonindustrial users means all other users of the treatment works other than industrial

users. Nonindustrial users are not subject to industrial cost recovery.

Normal domestic sewage means, for the purposes of determining surcharge, a

wastewater or sewage having an average daily suspended solids concentration of not more

than 250 mg/l, and average daily BOD of not more than 200 mg/l.

NPDES permit means a permit issued under the National Pollutant Discharge

Elimination System for discharge of wastewaters to the navigable waters of the United States

pursuant to section 402 of PL 92-500.

Operation and maintenance costs means all costs, direct and indirect, including

depreciation, necessary to insure adequate wastewater treatment on a continuing basis,

conforming with federal, state and local requirements, and assuring optimal long- term facility

management. Such costs shall not include debt service costs.

Person means any individual, firm, company, association, society, corporation or group

discharging any wastewater to the wastewater treatment works.

pH means the reciprocal of the logarithm of the hydrogen ion concentration. The

concentration is the weight of hydrogen ions in grams per liter of solution. The pH of any

discharge into the public sewer system shall not be less than five nor more than nine.

Pretreatment means the treatment of industrial sewage from privately owned industrial

sources prior to introduction into public treatment works.

Private sewer means a sewer which is not owned by a public authority.

Properly shredded garbage means the wastes from the preparation, cooking and

dispensing of food that have been shredded to such a degree that all particles will be carried

freely under flow conditions normally prevailing in public sewers, with no particle greater than

one inch in any dimension.

Public authority means any governmental agency having jurisdiction by law over

construction and use of a wastewater collection or treatment facility.

Public sewer means a sewer in which all owners of abutting properties have equal

rights, and which is owned and controlled by the public authority and will consist of the

following increments:

(1) Collector sewer means a sewer whose primary purpose is to collect

wastewaters from individual point source discharges.

(2) Interceptor sewer means a sewer whose primary purpose is to transport

wastewater from collector sewers to a treatment facility.

(3) Force main means a pipe in which wastewater is carried under pressure.

Pumping station means a station positioned in the public sewer system at which

wastewater is pumped to a higher level.

Replacement means expenditures for obtaining and installing equipment, accessories

or appurtenances which are necessary during the service life of the treatment works to

maintain the capacity and performance for which such works were designed and constructed.

Sanitary sewer means a sewer which carries sanitary and industrial wastes, and to

which stormwater, surface water and groundwater are not intentionally admitted.

Sewage means the combination of liquid and water carried wastes from residences,

commercial buildings, industrial plants and institutions. The three most common types of

sewage are:

(1) Sanitary sewage means the combination of liquid and water- carried wastes

discharged from toilet and other sanitary plumbing facilities.

(2) Industrial sewage means a combination of liquid and water- carried wastes,

discharged from any industrial establishment, and resulting from any trade or

process carried on in that establishment, including wastes from pretreatment

facilities and polluted cooling water.

(3) Combined sewage means wastes including sanitary sewage, industrial sewage,

stormwater, infiltration and inflow carried to the wastewater treatment facilities

by a combined sewer.

Sewer means a pipe or conduit for carrying sewage.

Significant industry means any industry that will contribute greater than ten percent of

the design flow and/or design pollutant loading of the treatment works.

Slug means any discharge of water or wastewater which in concentration of any given

constituent or in quantity of flow exceeds for any period of duration longer than 60 minutes

more than 2.5 times the average 24-hour concentration or flows during normal operation and

shall adversely affect the wastewater treatment facility.

Standard Methods means the laboratory procedures set forth in the latest edition, at the

time of analysis, of the Standard Methods for the Examination of Water and Wastewater

prepared and published jointly by the American Public Health Association, the American Water

Works Association and the Water Pollution Control Federation.

Storm sewer means a sewer for conveying water, groundwater or unpolluted water

from any source and to which sanitary and/or industrial wastes are not intentionally admitted.

Suspended solids means the solids that either float on the surface of, or are in

suspension in water, sewage or other liquids and which are removable by laboratory filtering.

Total solids means the sum of suspended and dissolved solids.

Toxic amount means the concentration of any pollutant or combination of pollutants

which upon exposure to or assimilation into any organism will cause adverse effects, such as

cancer, genetic mutations and physiological manifestations as defined in standards issued

pursuant to section 307(a) of PL 92-500.

Unpolluted water means water of quality equal to or better than the effluent criteria in

effect, or water that would not cause violation of receiving water quality standards and would

not be benefitted by discharge to the sanitary sewers and wastewater treatment facilities

provided.

Volatile organic matter means the material in the sewage solids transformed to gases

or vapors when heated at 550 degrees Celsius for 15 to 20 minutes.

Wastewater treatment works or sewage works means the structures, equipment and

processes required to collect, transport and treat domestic and industrial wastes and dispose

of the effluent and accumulated residual solids.

Waterworks means all facilities for water supply, filtration plant, storage reservoirs,

water lines and services and booster stations for obtaining, treating and distributing potable

water.

(Ord. No. 81-11-2, § 24-80, 11-3-81)

Cross references: Definitions and rules of construction generally, § 1-2.

Sec. 24-81. Privies, septic tanks, cesspools, etc.; construction and maintenance.

It shall be unlawful to construct or maintain any privy, privy vault, septic tank, cesspool

or other facility intended or used for the disposal of sewage, except as provided in this article.

(Code 1970, § 24-79; Ord. No. 81-11-2, § 24-81, 11-3-81)

Sec. 24-82. Separate and independent building sewer.

A separate and independent building sewer shall be provided for every building; except

where one building stands at the rear of another on an interior lot and no private sewer is

available or can be constructed to the rear building through an adjoining alley, court, yard or

driveway, the building sewer from the front building may be extended to the rear building and

the extension considered as the building sewer for the rear building; and except that

multifamily dwelling units, including apartments and mobile home trailer parks, may use a

single common building sewer for drainage of individual dwelling units.

(Code 1970, § 24-80; Ord. No. 81-11-2, § 24-82, 11-3-81)

Sec. 24-83. Location of sewers.

All sewers laid or constructed in any street or alley of the city shall be laid 15 feet north

of the center of any street running east and west, and 15 feet east of the center of any street

running north and south, and five feet north of the center of any alley running east and west,

and five feet east of the center of any alley running north and south.

(Code 1970, § 24-81; Ord. No. 81-11-2, § 24-83, 11-3-81)

Sec. 24-84. Diameter, slope; depth.

The size and slope of building sewers shall be subject to the approval of the inspector,

but in no event shall the diameter be less than four inches. The slope of such four-inch pipe

shall not be less than one-eighth inch per foot. A slope of one-fourth inch per foot shall be

used wherever practical.

(Code 1970, § 24-82; Ord. No. 81-11-2, § 24-84, 11-3-81)

Sec. 24-84a. Size, slope, alignment.

The size, slope, alignment and materials of construction of a building sewer, and the

methods to be used in excavating, placing of the pipe, jointing, testing and backfilling the

trench, shall all conform to the requirements of the building and plumbing code or other

applicable rules and regulations of the city. In the absence of code provisions, or in

amplification thereof, the materials and procedures set forth in appropriate specifications of the

American Society for Testing and Materials, Water Pollution Control Federation Manual of

Practice No. 9, and Standard Specifications for Water and Sewer Main Construction in Illinois

shall apply.

(Ord. No. 81-11-2, § 24-84(a), 11-3-81)

Sec. 24-85. Connection to sewer line.

The owner of all houses, buildings or properties used for human occupancy,

employment, recreation or other purposes situated within the jurisdiction of the city and

abutting any street, alley or right-of-way in which there is now located, or may in the future be

located, a public sewer of the city is hereby required, at his expense, to install suitable sanitary

facilities therein, and to connect such facilities directly with the proper public sewer in

accordance with the provisions of this article, within 60 days after the date of official notice to

do so, provided that the public sewer is within 200 feet of the property line.

(Code 1970, § 24-83; Ord. No. 81-11-2, § 24-85, 11-3-81)

Sec. 24-86. Private property to be connected by laterals.

The drainage of all private property into public sewers shall be effected by lateral

sewers.

(Code 1970, § 24-84; Ord. No. 81-11-2, § 24-86, 11-3-81)

Sec. 24-87. Intersections of laterals and mains.

All lateral sewers at their intersections with the main sewer shall, if necessary, be

curved toward the lower end of the sewer to lessen the obstruction of the current in the main

sewer by the influx from such lateral sewers.

(Code 1970, § 24-85; Ord. No. 81-11-2, § 24-87, 11-3-81)

Sec. 24-88. Building sewer.

The building sewer shall be constructed of either vitrified clay sewer pipe and fittings

meeting the current A.S.T.M. Specifications for Extra Strength Clay Sewer Pipe, or extra heavy

cast iron soil pipe and fittings meeting the current A.S.T.M. Specifications for Extra Heavy Cast

Iron Soil Pipe, or ABS (Acrylonitrile-Butadiene-Styrene) extra strength solid wall pipe and

fittings meeting the current A.S.T.M. Specifications for ABS Extra Strength Solid Wall Pipe. If

installed in filled or unstable ground, the building sewer shall be of cast iron soil pipe, except

that vitrified clay pipe or ABS solid wall pipe meeting the above specification requirements may

be accepted if laid on a suitable improved bed or cradle as approved by the inspector.

(Code 1970, § 24-86; Ord. No. 81-11-2, § 24-88, 11-3-81)

Sec. 24-89. Pipes near water pipes.

Any part of the building sewer that is located within ten feet of a water service pipe shall

be constructed of cast iron soil pipe with leaded joints.

(Code 1970, § 24-87; Ord. No. 81-11-2, § 24-89, 11-3-81)

Sec. 24-90. Damage by tree roots; pipe required.

Cast iron pipe with leaded joints may be required by the superintendent where the

building sewer is exposed to damage by tree roots.

(Code 1970, § 24-88; Ord. No. 81-11-2, § 24-90, 11-3-81)

Sec. 24-91. When in filled, unstable ground.

If installed in filled or unstable ground, the building sewer shall be of cast iron soil pipe,

except that a nonmetallic pipe may be accepted if laid on a suitable concrete bed or cradle

approved by the superintendent.

(Code 1970, § 24-89; Ord. No. 81-11-2, § 24-91, 11-3-81)

Sec. 24-92. Joints.

(a) All joints and connections shall be made gastight and watertight. Vitrified clay sewer

pipe shall be fitted with factory made resilient compression joints meeting the current

A.S.T.M. Specifications for Vitrified Clay Pipe Joints Having Resilient Properties.

(b) Before joining the pipe in the trench, the bell and spigot surfaces shall be wiped free of

dirt or other foreign matter. A lubricant or sealer as recommended by the pipe

manufacturer shall be applied to the bell and spigot mating surfaces just before they

are joined together. The spigot end shall be positioned into the bell end of the pipe

previously laid and shall then be shoved home to compress the joint and to assure a

tight fit between the interfaces.

(c) Joints for cast iron soil pipe shall be made by inserting a roll of hemp or jute and

thoroughly caulking it into place and then following with pure molten lead well caulked,

not less than one inch deep. No paint, varnish or putty will be allowed in the joints until

they have been tested and approved.

(Code 1970, § 24-90; Ord. No. 81-11-2, § 24-92, 11-3-81)

Sec. 24-93. Backflow protection.

Where the plumbing system or the subsoil drain of any premises are subjected to

backflow of water or sewage, the owner of the premises shall install a satisfactory backwater

valve or other satisfactory means of preventing such backflow.

(Code 1970, § 24-91; Ord. No. 81-11-2, § 24-93, 11-3-81)

Sec. 24-94. Placement of building sewer.

Whenever possible the building sewer shall be brought to the building at an elevation

below the basement floor, the depth shall be sufficient to afford protection from frost. All

excavations required for the installation of a building sewer shall be open trench work unless

otherwise approved by the inspector. Pipe laying and backfill shall be performed in accordance

with current A.S.T.M. Specification Designation C12, except that no backfill shall be placed

until the work has been inspected by the inspector or his representative.

(Ord. No. 81-11-2, § 24-94, 11-3-81)

Sec. 24-95. Lifting.

In all buildings in which any building drain is too low to permit gravity flow to the public

sewer, sanitary sewage carried by such drains shall be lifted by approved artificial means and

discharged to the building sewer. No water-operated sewage ejector shall be used.

(Ord. No. 81-11-2, § 24-95, 11-3-81)

Sec. 24-96. Impermissible connections.

No person shall make connection of roof downspouts, exterior foundation drains,

areaway drains or other sources of surface runoff or groundwater to a building sewer or

building drain which in turn is connected directly or indirectly to a public sanitary sewer.

(Ord. No. 81-11-2, § 24-96, 11-3-81)

Sec. 24-97. Manner of connection.

The connection of a building sewer into the public sewer shall be made at a "Y" branch

or "T" branch, if such a branch is available at a suitable location. If the public sewer has no

properly located "Y" or "T" branch available, the owner shall at his expense, install a "Y" branch

or a "Y" saddle fitting (for ABS truss pipe) at the location specified by the inspector. Under no

circumstances will the sewer service protrude into the sewer main to which the connection is

made. The invert of the building sewer at the point of connection shall be at the same or at a

higher elevation than the invert of the public sewer. A smooth, neat joint shall be made and the

connection made secure and watertight by encasement in concrete. Special fittings may be

used for the connection only when approved by the inspector. Manholes shall be constructed

at any junction of an eight-inch diameter line or larger into a public sewer.

(Ord. No. 81-11-2, § 24-97, 11-3-81)

Sec. 24-98. Notification for inspection.

The applicant for the building sewer shall notify the superintendent when the building

sewer is ready for inspection and connection to the public sewer. The connection shall be

made under the supervision of the superintendent or his representative.

(Ord. No. 81-11-2, § 24-98, 11-3-81)

Sec. 24-99. Guarding of excavations.

All excavations for building sewer installation shall be adequately guarded with

barricades and lights so as to protect the public from hazard. Streets, sidewalks, parkways and

other public property disturbed in the course of the work shall be restored in a manner

satisfactory to the city.

(Ord. No. 81-11-2, § 24-99, 11-3-81)

Sec. 24-100. Extension of public sewer.

The city shall be responsible for determining whether or not an extension of a public

sewer is economically feasible based on the estimated cost of the extension and the number

of existing potential users that will use said sewer line. If the extension is economically

feasible, then the city may install and pay the cost of the extension at the discretion of the city.

If the city elects not to pay the cost of extending the public sewer, then the person or persons

desiring sewer service shall install the extension at their own personal expense upon written

consent of the city. The city shall not pay for any extensions to an undeveloped area, such as

a subdivision being developed, unless there are sufficient existing residents or businesses to

make the extension economically feasible.

(Ord. No. 81-11-2, § 24-100, 11-3-81)

Sec. 24-101. Approval of extension plans.

The city must approve all plans and specifications for any extensions. Before any

extensions are installed, the plans and specifications must be reviewed and approved by the

state environmental protection agency.

(Ord. No. 81-11-2, § 24-101, 11-3-81)

Sec. 24-102. Right-of-way.

Ownership rights-of-way and title must be conveyed to the city for all extensions

installed by anyone other than the city. The city shall maintain the extended public sewers

thereafter.

(Ord. No. 81-11-2, § 24-102, 11-3-81)

Sec. 24-103. Capacity of system.

No extension of the public sewer will be permitted if, in the opinion of the city, the

system does not have the necessary capacity to serve the proposed extension.

(Ord. No. 81-11-2, § 24-103, 11-3-81)

Sec. 24-104. Additional requirements.

No statement contained in this division shall be construed to interfere with any

additional requirements that may be imposed by the health officer, or superintendent of water

and sewers.

(Code 1970, § 24-92; Ord. No. 81-11-2, § 24-104, 11-3-81)